## Sheet1
MOLALLA WASTEWATER TREATMENT PLANT DISCHARGE MONITORING REPORT | [20 empty] | RECEIVING WATERS: BEAR CREEK (BC)
CITY OF MOLALLA |  |  |  |  | CLACKAMAL COUNTY OREGON | [9 empty] | PERMIT # 100893 | [5 empty] | FILE # 57613 |  |  | TREATMENT SYS. CLASS: III |  |  |  |  | III |  | REMARKS, explanation of exceeding permits:
POPULATION 5300 |  |  |  | TREATMENT PROCESS: PRE-AERATED LAGOONS WITH EFFLUENT FILTRATION | [19 empty] | COLLECTION SYS. CLASS: III |  |  |  |  | II
|  |  |  | PLANT INFLUENT |  |  |  | PLANT EFFLUENT @ DMS
|  |  | MOL. |  | BOD | TSS |  |  |  | DO | BOD | BODBOD | BOD |  | TSS |  | TSS | TSS | CHLORINE |  | BACTERIA |  |  |  |  | Aer Basin |  | Lagoons
| INF. | EFF. | River | [8 empty] | Rem | disch. | NH3 |  | TSS | Remov. | disch. | USED | RESID. | TOTAL | E. coli |  |  |  | DO |  | Cell | Cell | RAIN
DAY | MGD | MGD | CFS | pH | mg/L | mg/L | Temp. | pH | temp | mg/L | mg/L | % | lb. | mg/L | mg/L | mg/L | % | lb. | lb. | mg/L | COLIF. |  |  |  |  | mg/L | temp | #1,ft. | #2, ft. | in.
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
TOTAL | 0 | 0 | 0 | [9 empty] | 0 |  |  |  |  | 0 | 0 | [10 empty] | 0
MAX | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
MIN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
AVG | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #NUM! | #NUM! |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
PERMIT |  |  |  | 6- |  |  |  | 6- |  |  | 10 | 85% | 320 |  |  | 10 | 85% | 320 |  |  | 23 | 126
STAND |  |  |  | 9 |  |  |  | 9 |  |  | mg/L |  | lb/day |  |  | mg/L |  | lb/day |  |  | /100ml | /100ml
PRINCIPAL OPERATOR NAME: Dennis M St. Clair |  |  |  | Otis Phillips | [8 empty] | TREATMENT CERTIFICATION # AND GRADE: | [7 empty] | 10506 | / | LEVEL 2 | 4
SIGNATURE: | [12 empty] | COLLECTIONS CERTIFICATION # AND GRADE: | [7 empty] | 7848 | / | LEVEL 1
During this reporting period did all monitoring data & sampling frequencies meet permit requirments & limits (if "no", explain)? | [24 empty] | Yes / No
During this reporting period were there unanticipated bypasses or upsets which exceeded any effluent limits (if "yes", explain)? | [25 empty] | Yes / No
During this reporting period was there any collections system overflows (if "yes" explain)? | [19 empty] | Yes / No

## Sheet2
MOLALLA WASTEWATER TREATMENT PLANT DISCHARGE MONITORING REPORT | [13 empty] | RECEIVING WATERS: MOLALLA RIVER | [10 empty] | MONTH:
CITY OF MOLALLA |  |  |  | CLACKAMAS COUNTY OREGON | [9 empty] | PERMIT #100893 |  |  | FILE #57613 |  | TREATMENT SYS. CLASS III | [5 empty] | REMARKS
POPULATION 6500 |  |  |  | TREATMENT PROCESS: PRE-AERATED LAGOONS WITH EFFLUENT FILTRATION | [14 empty] | COLLECTION SYS. CLASS II
|  |  |  | PLANT INFLUENT |  |  |  | PLANT EFFLUENT @DMS
MOL RIVER
DAY | INF. MGD | EFF. MGD | Molalla River CFS | pH | BOD mg/L | TSS mg/L | Temp | pH | Max Temp | Min DO | NH3 | BOD mg/L | BOD % Rem | BOD Disch. lbs | TSS mg/L | TSS % Rem | TSS Disch. Lbs | Chlorine Used lbs | Max Chlorine Hr. Avg | Total Colif | Ecoli | 1400- DO | 1800 Temp | RAIN inch
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
Total
MAX
MIN
AVG
Permit Stand

## DMR 2007
MOLALLA WASTEWATER TREATMENT PLANT DISCHARGE MONITORING REPORT | [13 empty] | RECEIVING WATERS: MOLALLA RIVER | [12 empty] | February | 2011 | MOLALLA WASTEWATER TREATMENT PLANT
CITY OF MOLALLA |  |  |  | CLACKAMAS COUNTY OREGON | [9 empty] | PERMIT #101514 |  |  | FILE #57613 |  | TREATMENT SYS. CLASS III | [7 empty] | REMARKS |  | CITY OF MOLALLA
POPULATION: 7800 |  |  |  | TREATMENT PROCESS: PRE-AERATED LAGOONS WITH EFFLUENT FILTRATION | [14 empty] | COLLECTION SYS. CLASS II | [9 empty] | DMS Chlorine readings
|  |  |  | PLANT INFLUENT |  |  |  | PLANT EFFLUENT @DMS
DAY | INF. MGD | EFF. MGD | Molalla River CFS | Temp | pH | BOD mg/L | TSS mg/L | pH | Min DO | Max Temp | NH3 | BOD mg/L | BOD % Rem | BOD Disch. lbs | TSS mg/L | TSS % Rem | TSS Disch. Lbs | Chlorine Used lbs | Max Chlorine Hr. Avg | E.coli | Turb- idity | MOL 1400- DO | River 1800 Temp | RAIN inch | Pond 1 Feet | Pond 2 Feet |  |  | DAY | Max Pre Dechlor Hr. Ave. | Pre Dechlor Grab | Max Post Dechlor Hr. Ave. | Post Dechlor Grab
1 | 1.355 | 1.996 | 738 | 13.4 |  | 157.6 | 313 |  | 11.68 | 9 |  | 2.21 | 99 | 36.6 | 1.5 | 99 | 25 | 20 | 0 |  | 0.66 | 12.21 | 6.3 |  | 9.2 | 11.2 | Installed actuator in #2 filter. (4 filters) |  | 1 | 0.79 | 0.18 | 0 | 0
2 | 1.323 | 2.674 | 661 | 13.8 | 7.5 |  |  | 7.5 | 11.84 | 8.5 | [7 empty] | 29 | 0 |  | 0.74 | 12.31 | 5.5 |  | 8.9 | 11.2 |  |  | 2 | 0.86 | 0.4 | 0 | 0.02
3 | 1.277 | 2.869 | 602 | 13.2 |  | 156.6 | 151 |  | 12 | 8.2 | 6 | 2.26 | 99 | 54 | 1.5 | 99 | 36 | 29 | 0 | 2 | 0.76 | 12.54 | 5.3 |  | 8.7 | 10.9 |  |  | 3 | 0.86 | 0.26 | 0 | 0
4 | 1.274 | 2.767 | 553 | 13.6 | 7.8 |  |  | 7.6 | 12.12 | 8 | [7 empty] | 31 | 0 |  | 0.69 | 11.81 | 7.2 | 0.03 | 8.4 | 10.7 |  |  | 4 | 1.5 | 0.64 | 0 | 0
5 | 1.295 | 2.791 | 553 | [5 empty] | 12.02 | 8.4 | [7 empty] | 28 | 0 |  | 0.71 |  |  | 0.05 |  |  |  |  | 5 | 1.49 | 0.49 | 0 | 0.05
6 | 1.347 | 2.756 | 605 | [5 empty] | 11.82 | 8.8 | [7 empty] | 13 | 0 |  | 0.7 |  |  | 0.05 |  |  |  |  | 6 | 1.46 | 0.59 | 0 | 0
7 | 1.316 | 2.671 | 630 | 13.6 | 7.5 |  |  | 7.6 | 11.82 | 8.8 | 7.8 | [6 empty] | 24 | 0.01 | <1 | 0.69 | 11.42 | 8.9 | 0.1 | 8.2 | 10.1 |  |  | 7 | 1.44 | 0.08 | 0.01 | 0.01
8 | 1.339 | 2.527 | 683 | 13.5 |  | 90.7 | 265.5 |  | 11.95 | 8.6 |  | 4.7 | 95 | 99 | 0.7 | 99 | 14.7 | 35 | 0 |  | 0.69 | 12.28 | 7.2 |  | 8 | 9.8 |  |  | 8 | 1.35 | 0.5 | 0 | 0
9 | 1.274 | 2.603 | 630 | 13.4 | 7.6 |  |  | 7.5 | 11.91 | 8.4 | [7 empty] | 26 | 0.09 |  | 0.72 | 12.24 | 6.4 |  | 7.9 | 9.6 |  |  | 9 | 1.03 | 0.53 | 0.09 | 0
10 | 1.227 | 2.582 | 582 | 13.3 |  | 225.4 | 244.5 |  | 11.91 | 8.3 | 6.7 | 2.3 | 99 | 49.5 | 0.3 | 99 | 6.5 | 28 | 0.1 | <1 | 0.79 | 12.01 | 6.5 |  | 7.7 | 9.4 |  |  | 10 | 1.02 | 0.47 | 0.1 | 0
11 | 1.201 | 2.583 | 557 | 13.7 | 7.7 |  |  | 7.8 | 11.85 | 8.4 | [7 empty] | 32 | 0.1 |  | 0.73 | 11.68 | 7.2 |  | 7.6 | 9.2 | Closed pond #1 eff valve 15 turns |  | 11 | 1 | 0.14 | 0.1 | 0.06
12 | 1.343 | 2.483 | 550 | [5 empty] | 11.69 | 8.6 | [7 empty] | 39 | 0.1 |  | 0.74 |  |  | 0.8 |  |  |  |  | 12 | 0.28 | 0.08 | 0.1 | 0.03
13 | 1.001 | 2.363 | 827 | [5 empty] | 11.9 | 8.4 | [7 empty] | 15 | 0.1 |  | 0.83 |  |  | 0.1 |  |  |  |  | 13 | 0.29 | 0.04 | 0.1 | 0.01
14 | 1.967 | 2.1 | 898 | 12.7 | 7.4 |  |  | 7.7 | 11.7 | 8.6 | 8.6 | [6 empty] | 33 | 0.1 | <1 | 1.01 | 10.95 | 9 | 0.8 | 8.4 | 7.7 | Alkalinity 77.1 |  | 14 | 0.28 | 0 | 0.1 | 0
15 | 2.887 | 1.904 | 1950 | 11.5 |  | 73.9 | 285 |  | 11.8 | 8.6 |  | 3.7 | 95 | 58.7 | 0.2 | 99 | 3.2 | 31 | 0.01 |  | 0.92 | 11.4 | 7.3 | 0.2 | 8.7 | 7.6 | Opened pond #1 eff. valve 12 turns |  | 15 | 1.06 | 0.54 | 0.01 | 0.01
16 | 2.469 | 1.905 | 2370 | 12.1 | 7.2 |  |  | 7.8 | 11.9 | 8.3 | [7 empty] | 22 | 0.02 |  | 0.9 | 11.9 | 6.2 | 0.01 | 8.5 | 7.6 |  |  | 16 | 1.05 | 0.39 | 0.02 | 0.02
17 | 2.096 | 1.937 | 1800 | 12.2 |  | 54.4 | 144.5 |  | 12 | 8.1 | 9.5 | 3.9 | 92 | 64 | 1.2 | 99 | 19 | 21 | 0.01 | <1 | 1.05 | 12.39 | 6.3 |  | 8.8 | 7.7 | Opened pond #1 eff. valve 5 turns |  | 17 | 0.79 | 0.38 | 0.01 | 0
18 | 1.893 | 1.982 | 1390 | 11.9 | 7.4 |  |  | 7.9 | 12.05 | 8.1 | [7 empty] | 28 | 0.03 |  | 1.03 | 11.3 | 7.2 | 0.2 | 8.6 | 7.7 |  |  | 18 | 0.77 | 0.2 | 0.03 | 0.03
19 | 1.84 | 2.057 | 1150 | [5 empty] | 12.18 | 7.8 | [7 empty] | 25 | 0.03 |  | 0.91 | [7 empty] | 19 | 0.39 | 0.32 | 0.03 | 0.02
20 | 1.705 | 2.068 | 966 | [5 empty] | 12.22 | 7.8 | [7 empty] | 16 | 0.04 |  | 1.23 |  |  | 0.05 |  |  |  |  | 20 | 0.37 | 0.31 | 0.04 | 0.05
21 | 1.619 | 2.059 | 827 | 12.7 | 7.6 |  |  | 7.8 | 12.21 | 7.8 | 11.3 | [6 empty] | 23 | 0.02 | <1 | 1.03 | 12.29 | 6.2 |  | 7.8 | 7.9 |  |  | 21 | 1.09 | 0.54 | 0.02 | 0
22 | 1.572 | 2.005 | 745 | 12.5 |  | 166.2 | 155 |  | 12.16 | 8.1 |  | 4.41 | 97 | 73.7 | 1.2 | 99 | 20.1 | 25 | 0.03 |  | 1.21 | 11.34 | 7 | 0.1 | 7.5 | 8 | Closed pond #1eff. valve 6 turns |  | 22 | 1.02 | 0.31 | 0.03 | 0.03
23 | 1.655 | 1.981 | 685 | 12.8 | 7.6 |  |  | 7.8 | 12.4 | 7.2 | [7 empty] | 23 | 0.06 |  | 1.11 | 12.23 | 5.2 | 0.2 | 7.4 | 8.1 |  |  | 23 | 1.04 | 0.46 | 0.06 | 0.05
24 | 1.686 | 1.944 | 656 | 11.9 |  | 119.8 | 123 |  | 12.4 | 7.2 | 6.6 | 3.2 | 97 | 52.5 | 0.3 | 99 | 4.9 | 22 | 0.06 | <1 | 0.8 | 12.88 | 4.4 | 0.1 | 7.3 | 7.9 |  |  | 24 | 1.04 | 0.45 | 0.06 | 0.04
25 | 1.611 | 1.838 | 577 | 12.1 | 7.6 |  |  | 7.7 | 12.4 | 6.8 | [7 empty] | 26 | 0.07 |  | 0.71 | 12.9 | 4.2 |  | 7.3 | 7.8 |  |  | 25 | 1.05 | 0.42 | 0.07 | 0
26 | 1.516 | 1.759 | 509 | [5 empty] | 12.48 | 6.4 | [7 empty] | 23 | 0.06 |  | 0.79 | [7 empty] | 26 | 1.1 | 0.61 | 0.06 | 0.01
27 | 1.519 | 1.397 | 507 | [5 empty] | 12.65 | 5.6 | [7 empty] | 22 | 0.05 |  | 0.64 |  |  | 0.3 |  |  |  |  | 27 | 1.1 | 0.62 | 0.05 | 0
28 | 3.606 | 1.397 | 1190 | 11 | 7.3 |  |  | 7.7 | 12.9 | 5.5 | 10.3 | [6 empty] | 20 | 0 | <1 | 0.68 | 12.88 | 3.5 | 2.7 | 7.2 | 7.6 |  |  | 28 | 1.03 | 0.42 | 0 | 0.01
29 | [28 empty] | 29
30 | [28 empty] | 30
31 | [28 empty] | 31
Total | 46.213 | 61.998 | [15 empty] | 709 | [5 empty] | 5.79 |  |  |  |  | Total | 26.55 | 10.37 | 1.09 | 0.45
MAX | 3.606 | 2.869 | 2370 | 13.8 | 7.8 | 225.4 | 313 | 7.9 | 12.9 | 9 | 11.3 | 4.7 | 99 | 99 | 1.5 | 99 | 36 | 39 | 0.1 |  |  | 12.9 | 9 | 2.7 | 9.2 | 11.2 |  |  | MAX | 1.5 | 0.64 | 0.1 | 0.06
MIN | 1.001 | 1.397 | 507 | 11 | 7.2 | 54.4 | 123 | 7.5 | 11.68 | 5.5 | 6 | 2.21 | 92 | 36.6 | 0.2 | 99 | 3.2 | 13 | 0 |  |  | 10.95 | 3.5 | 0.01 | 7.2 | 7.6 |  |  | MIN | 0.28 | 0 | 0 | 0
AVG | 1.6505 | 2.2142 | 871.1071 | 12.745 | 7.5167 | 130.575 | 210.1875 | 7.7 | 12.07 | 7.9393 | 8.35 | 3.335 | 96.625 | 61 | 0.8625 | 99 | 16.175 | 25.3214 | 0.038929 | 2 | 0.83821 | 12.048 | 6.35 | 0.36188 | 8.105 | 8.885 |  |  | AVG | 0.94821 | 0.37036 | 0.038929 | 0.016071
PERMIT | [7 empty] | 6- |  |  | 16.7mg/L | 10mg/L | 80% | 160 | 10mg/L | 80% | 160 |  | 0.07mg/L | 126/ | [8 empty] | PERMIT #101514
STAND | [7 empty] | 9 |  |  | Mo/Avg | Mo/Avg | Mo/Avg | lbs/day | Mo/Avg | Mo/Avg | lbs/day |  | Mo/Avg | 100ml
I CERTIFY, UNDER PENALTY OF LAW, THAT THIS DOCUMENT AND ALL ATTACHMENTS WERE PREPARED UNDER MY DIRECTION OR SUPERVISION IN ACCORDANCE WITH A SYSTEM DESIGNED TO ASSURE THAT QUALIFIED PERSONNEL
PROPERLY GATHER AND EVALUATE THE INFORMATION SUBMITTED. BASED ON MY INQUIRY OF THE PERSON OR PERSONS WHO MANAGE THE SYSTEM, OR THOSE PERSONS DIRECTLY RESPONSIBLE FOR GATHERING THE INFORMATION, THE
INFORMATION SUBMITTED IS, TO THE BEST OF MY KNOWLEDGE AND BELIEF, TRUE, ACCURATE, AND COMPLETE. I AM AWARE THAT THERE ARE SIGNIFICANT PENALTIES FOR SUBMITTING FALSE INFORMATION, INCLUDING THE POSSIBILITY OF
FINES AND IMPRISONMENT FOR KNOWING VIOLATIONS.
[7 empty] | OPERATOR NAME |  |  |  | TERRY HINZMAN | [6 empty] | TREATMENT CERTIFICATION # & GRADE | [7 empty] | 9980 | LEVEL 4
[7 empty] | SIGNATURE | [10 empty] | COLLECTION CERTIFICATION # & GRADE | [7 empty] | 7991 | LEVEL 2